## Slide 1: Supermarket’s Energy Recovery: Waste Heat for District Heating Networks
Student : Lugas Raka Adrianto
Supervisor : Samer Sawalha
May 2017
MJ1432 – Practical Energy Related Project
Notes: Good morning everyone.
Continuing to what I have presented couple of weeks ago, in this opportunity I would like to share to all of you the main findings which I have obtained from several discussions and revision along the way of this project with my supervisor.
Again, the broad subject of this project would belong to energy efficiency, which is regarded as one of the cheapest form of energy being wasted out there.
Specifically, the main object of this project is digging deep into a commercial place where most of us would go to find grocery, namely supermarket.
To know more about why this place becomes so interesting in my project, first let me proceed with the outline

## Slide 2: Outline
Introduction
  Recovering Energy Loss in the Society
  CO2 as refrigerant in supermarket systems
Project Overview and Objectives
Methodology
Main Studies and Findings
Conclusion
Notes: At the beginning, I will provide brief overview of the possible energy recovery around us, in general of course. To get better understanding on the possible solutions to increase energy efficiency.
Secondly, you will be given a concise information on the background of this project in relation to the supermarket, as well as the latest development of using CO2 (or commonly known as R744 in the refrigeration topic) as the novel refrigerant with relatively low level of GWP.
Afterwards, definitely the main objective of the project with the approach which has been taken will also be elaborated, since it defines the way I structure and organize the main findings in the next section.
The results would revolve mainly on comparing different scenarios, which all of you would know from the project overview.
Compiling all the results and analyzing It thoroughly will later help me to summarize all of it for a firm conclusion at the last part.

## Slide 3: Background of Project
Ground Temperature in Summer
Supermarkets
Data Centers
Ice Rinks
Excess heat
Excess cold
District
Heating
District Cooling
Notes: As a quick summary, we all know that there are numerous strategies to recover loss of energy in our surroundings. The chart presented here, notably not limiting other possible solutions, is shown to just give you a general idea of energy recovery. For instance, supermarket where the refrigeration process takes place and dissipating lot of heat to the environment or abundant of cold ground during summer time, which we can exploit to receive cold energy for accomplishing thermal comfort. For the purpose of the study, the project will focus only on supermarkets energy recovery, especially projecting it towards district heating networks since it has a great potential other than using the recovered energy internally at the supermarket. In fact, the project to investigate heat recovery has also been started in Denmark and other Scandinavian countries as these countries have fairly mature district energy networks which connects almost every major buildings.

## Slide 4: Supermarket – Refrigeration System Improvement
Chart: 
| Refrigeration | Lighting | HVAC | Outdoor | Kitchen | Others
 | 0.47 | 0.27 | 0.13 | 0.05 | 0.03 | 0.05
Typical energy consumption breakdown in Swedish supermarket
Nearly 50% belongs to refrigeration system
Arias, 2005
Heat recovery potential
200 – 300 MWh/ year
150 kW
Supermarket
Equivalent to 1200 tons of wood chips
Notes: Moving forward, as we take a closer look into the supermarket energy breakdown, it can be determined easily that refrigeration is one of the most energy demanding process compared to others, such as lighting, HVAC, kitchen, etc. Consuming nearly half of total energy required in the supermarket.
It becomes more appealing to investigate, remembering the number of supermarkets in Sweden reaches 3500 stores.
One simple calculation from previous study has revealed that for one medium-size supermarket with 150 kW cooling load, it holds the potential of 300 MWh/ year heat recovery. Imagine, taking the common case CHP district heating facility in Sweden, this energy is equivalent to 1200 ton of woodchips/ year.

## Slide 5: CO2 as the Main Refrigerant
What if?
Conventional System: CO2
Proposed System: CO2 (R-744)
Lower GWP (1 vs 3200)
Hypothesis: Lower energy consumption?
Sawalha, 2015
Notes: So what’s the deal with the current refrigeration system in the supermarket?
These figures show the side-side process flow diagram of common refrigeration system without and with energy recovery.
Left side – old system with R404 as the refrigerant (utilizing basic air gas cooler to reject heat)
Right side – incorporating additional exchangers just before air gas cooler, with the implication of running at higher pressure. There are two exchangers, which will become different scenario in the methodology (either SH, DH, SH+DH). It should also be noted this one is using CO2, with lower GWP with 3200 multiplier less than R404 (11% leakage from refrigeration system as the inevitable occurance)
As I mentioned before, higher pressure in these compressors means higher electricity input into the system, with possible benefit if the recovered heat is sufficient/ profitable enough.
Therefore, linking and connecting this novel configuration to the Fortum’s new business model becomes necessary to conduct, particularly for supermarket owners.

## Slide 6: Objectives & Methodology
Techno-economic analysis of CO2 refrigeration with optimum heat recovery scenario
Technical
Compressor duty
Heat duty (building, auxiliary heater)
Economic
Utility price (electricity, heat)
Outcomes
Operating cost (profit and loss analysis)
Selling of excess heat (profit)
District heating production
CO2 avoided
Cost of producing heat (COP relation)
MAIN OBJECTIVE
METHODOLOGY
EES©
Notes: THe main goal  finding the best scenario to retrieve usual rejected heat to the surroundings, following the pfd in the previous slides. Best is defined as the most economic operating costs as well as the avoided CO2 if one such system is preferred.
As for the steps/ paths to achieve that main goal, three of these blocks would have to be evaluated sequentially since the value or results of one block influence the upcoming block.
Technical  using EES mainly, build the correct model to rigorously simulate the cycle (condition from business partners and previously finished project/ thesis)
Economic -> Utility price, mainly Fortum for Open District heating
Outcomes  OPEX, avoided CO2

## Slide 7: Results: Comparison of Cost
Chart: Operating Cost (Million SEK)
| Default Case | With Heat Pump | DH Only | SH Only | SH + DH, Auxiliary | SH + DH, No Auxiliary
100 kW Cooling Load | 0.461 | 0.33291 | 0.61943 | 0.30216 | 0.2977 | 0.29762
150 kW Cooling Load | 0.54317 | 0.41508 | 0.77731 | 0.38353 | 0 | 0.3898
Implementing Heat Recovery could:
Save up to 163k SEK
*Utility costs: Electricity (1500 SEK/ MWh), Heat (770 SEK/ MWh) – Fortum, 2017
36%
30%
Calculated Savings
Notes: Here we have reached one of the main findings of this project.
In this figure, all of possible scenario is presented with 2 different cooling load (small and medium sized supermarkets)
First we have default case (just a basic one), 2ndly basic one + heat pump, and other four heat recovery scenarios..
DH stands for district heating, while SH stands for space heating/ buildings heating.
Comparing all scenario with default case  take least accumulated operating cost in this case (SH+DH no auxiliary) can save 36% of operating cost. This percentage is equal to 163k SEK for small sized supermarket.

## Slide 8: Which scenario is shown to be more efficient?
Chart: T outdoor, C
| 8 | 7 | 6 | 5 | 4 | 3 | 2 | 1 | 0 | -1 | -2 | -3 | -4 | -5 | -6 | -7 | -8 | -9 | -10 | -11 | -12 | -13 | -14 | -15
DH Only, T Return = 60 C | 702.7214 | 723.6237 | 743.9004 | 764.3336 | 765.8764 | 767.4508 | 768.3938 | 769.3548 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665 | 770.4665
DH Only, T Return = 55 C | 634.6662 | 652.8169 | 671.4607 | 690.2725 | 691.5138 | 692.7799 | 693.5308 | 694.2958 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946 | 695.1946
SH+DH No Auxiliary, T Return = 60 C | 566.9616 | 518.4348 | 476.2492 | 437.5585 | 401.3713 | 366.981 | 333.2516 | 301.0098 | 269.7722 | 243.9252 | 219.6247 | 196.942 | 176.63 | 158.8235 | 144.4216 | 135.0043 | 133.7969 | 150.8158 | 214.6873 | 246.4661 | 277.6017 | 307.5214 | 336.3394 | 364.4135
SH+DH No Auxiliary, T Return = 55 C | 520.3791 | 479.1173 | 441.2873 | 405.7506 | 371.7504 | 339.3109 | 307.6388 | 277.2571 | 248.1837 | 224.5728 | 202.6047 | 182.815 | 166.0975 | 152.7562 | 146.0362 | 152.8247 | 211.7127 | 240.0852 | 267.7104 | 294.1926 | 320.274 | 345.1855 | 369.3493 | 393.112
Fortum ODH | 259 | 259 | 259 | 259 | 259 | 277.9981 | 285.7254 | 293.4527 | 301.18 | 308.9073 | 316.6346 | 324.3619 | 332.0892 | 339.8165 | 347.5438 | 355.2711 | 362.9984 | 370.7257 | 378.453 | 386.1803 | 393.9076 | 401.6349 | 409.3622 | 417.0895
SH+ DH Case without auxiliary heater displays profitable model for this period
Producing heat between 1 and -15oC
Notes: The main reason behind this would be due to the fact that the cost of generating heat for district heating networks is less than the price that Fortum is willing to pay.
For this particular case with different T outdoor, it can be seen that SH+DH scenario outperforms DH only case since the supermarket can gain profit at this window of temperature(between 1 and -15 C).
Whenever Fortum price > cost of producing heat, the supermarket reaps benefit out of this heat recovery process.

## Slide 9: Potential Of Reducing CO2 emission
Chart: Emission Index
| Default Case | With Heat Pump | DH Only | SH Only | SH + DH, Auxiliary | SH + DH, No Auxiliary
100 kW Cooling Load | 80.0107 | 13.639 | 91.2598 | 12.3792 | 15.1157 | 15.0773
150 kW Cooling Load | 83.3772 | 17.0055 | 100 | 15.713 | 0 | 19.8609
Implementing Heat Recovery could:
Cut emission up to
83 tons CO2
100 Index = 129 tons CO2
Notes: As a complementary analysis, CO2 avoided analysis is also exercised in this project.
What I consider to calculate the CO2 here would be heating GHG emission and electricity GHG emission.
Including both of these values for each scenario, most importantly consumed energy from external system, gives the following chart.
Again, heat recovery case has revealed its prospect to cut down emission 80% in percentage (Why? Because heat recovery relies heavily on electricity with lower GHG emission in Sweden as opposed to receiving heat from DH with higher GHG emission)

## Slide 10: Summary of Main Findings
Waste Heat Recovery in Supermarket
Feasibility
Optimum Scenario
CO2 avoided
CO2 is a good candidate to replace conventional refrigerant
SH+ DH without Auxiliary heater is shown to be the most economical configuration
Implementing waste heat recovery system would enable GHG emission reduction, apart from refrigerant’s leakage
Notes: TO wrap up all discussion:
CO2 is promising refrigerant for future supermarket with great heat recoverability
SH+DH has proven to be the most economic configuration
CO2 savings is possible with heat recovery scenario, putting aside less GWP with CO2 as the refrigerant compared to the conventional R404 with 3200 GWP.

## Slide 11: Thank You
Further discussions?
Contact: adrianto@kth.se
Energy efficiency has always been the cheapest ‘form’ of energy
-ACEE, 2016
Notes: Thank you for all your attention, and now I would be glad to receive any of your feedback/ questions toward this project.